## Funks Creek
Site Reservoir Project
Flow Augmentation to Funks Creek
Sites to Funks Creek
Funks Creek WSE (ft) = | 260
Sites Reservoir WSE (avg) = | 450
Pipe Length (ft) = | 2800
Hazen-Williams C Value = | 135
Flow (cfs) = | 10 | 20 | 50 | 100 | 200 | 300 | 400 | 500
Pipe Diameter (in) = | 12 | 16 | 24 | 30 | 42 | 54 | 60 | 72
Pipe Velocity (ft/sec) = | 12.7324 | 14.3239 | 15.9155 | 20.3718 | 20.7876 | 18.8628 | 20.3718 | 17.6839
Pipe Friction Loss (ft) = | 105.6448 | 93.8214 | 70.9458 | 86.2741 | 60.4147 | 37.6164 | 38.342 | 23.8422
Minor Losses (ft) = | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Total Head Required (ft) | 110.6448 | 99.8214 | 77.9458 | 94.2741 | 69.4147 | 47.6164 | 49.342 | 35.8422
Available Head (ft) = | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
Head Left (ft) = | 79.3552 | 90.1786 | 112.0542 | 95.7259 | 120.5853 | 142.3836 | 140.658 | 154.1578
Pipe size okay? | yes | yes | yes | yes | yes | yes | yes | yes
Pipe Costs @( $20/di-lf) = | 672000 | 896000 | 1344000 | 1680000 | 2352000 | 3024000 | 3360000 | 4032000
Energy Dispipating Structure | 300000 | 300000 | 400000 | 500000 | 650000 | 800000 | 1000000 | 1200000
TOTAL | 972000 | 1196000 | 1744000 | 2180000 | 3002000 | 3824000 | 4360000 | 5232000
Assumptions
Elevation at turnout to Funks Creek is roughly at elevation 260 feet.
Unit cost for pipe is $20/diameter-inch per linear foot, which is same as used in original TM entitled Funks Creek Environmental Water Source Analysis dated October 12, 2020
Unit cost for disipating structure based on interpolating recent costs estimates for Dunnigan Pipeline.
Velocities in pipes are limited to approximately 20 feet per second